Stormwater harvesting in Alexandra and Queen Victoria Gardens

Case Study

Written for the Urban Water website in 2015

# Table of Contents

Fast facts	2

Project overview	2

How does the system work?	3

Stormwater harvesting system timeline	3

Project partners	4

Cost	4

Community benefits	4

Research and planning	4

Community consultation and engagement	5

Design challenges and constraints	5

Planning approval process	6

System components	6

Testing and commissioning	9

Ongoing management	9

Environmental impact	10

Lessons learnt	10

# Fast facts

Project title: 		Alexandra and Queen Victoria Gardens stormwater harvesting system

Project description: 	stormwater harvesting and biofiltration (stored in ponds)
Purpose: 		Alternative irrigation supply
Completion date: 	August 2013
Volume:	 	20 million litres
Catchment: 		34 hectares, 20% impervious, 47 million litres of rainwater each year 
Cost:  			$1.6 million

Address: 		St Kilda Road, South Yarra

# Project overview

Alexandra Gardens and Queen Victoria Gardens sit adjacent to each other on the southern bank of the Yarra River. They link the Domain Parklands with the central city and provide 10 hectares of green open space.

The Queen Victoria Gardens is known for sweeping lawns, colourful flower-beds and ornamental ponds. The Alexandra Gardens are known for palm-lined avenues and open lawns. Many high profile events are held at the gardens each year.

Providing enough water to keep both gardens healthy during the increasingly severe impacts of climate change, including drought, heat waves and water restrictions has been a challenge.

The Alexandra and Queen Victoria Gardens stormwater harvesting system captures, treats and stores 20 million litres of stormwater each year to be used for irrigation, reducing the potable water consumption in the garden by 55 per cent. The innovative system makes use of retrofitted ornamental ponds in Queen Victoria Gardens for storing stormwater.

The system is part of the Eastern Melbourne Parks and Gardens Stormwater Harvesting Scheme. Overall, the Scheme received $4.8 million in funding from the Australian Government’s Water for the Future initiative.

## What benefits has the stormwater harvesting system provided?

- Saved 20 million litres of drinking water per year;

- Provided a reliable alternative water source to irrigate the gardens;

- Contributed 1.19 per cent towards the Council’s 30 per cent alternative water use target by 2018 under our Total Watermark Strategy;

- Reduced pollutant levels of nitrogen, phosphorus, heavy metals and sediment entering the Yarra River and Port Phillip Bay.

# How does the system work?

Water is diverted from the existing drains beneath Queen Victoria Gardens into a gross pollutant trap where large items, such as leaves and litter, are removed from the water. Next, a long sedimentation chamber settles out small particle pollution, including fine sand and oil.

A pump transfers the water to a series of three ponds, which we retrofitted for stormwater harvesting. When the water level in the ponds reaches a certain threshold, it is pumped across to Alexandra Gardens for treatment, via a pipe under Alexandra Avenue.

In Alexandra Gardens, a biofiltration garden bed naturally removes pollutants from the water as it seeps through the soil and plant root systems. The clean water is collected under the bed in a pump well and transferred to an above ground storage tank. The tank stores 230 kilolitres of water for irrigation. Excess clean water is returned to the Yarra River via the stormwater drains.

# Stormwater harvesting system timeline

Research and planning		November 2008 – February 2012

Geotechnical survey			January 2009

Funding application			February 2010

Funding approval 			March 2011

Concept designs 			February 2012

Detailed designs			March 2013

Construction 				November 2012 – December  2013

Commissioning 			December 2013 – June 2014

# Project partners

A broad range of specialties were required to complete this project, including:

- Funding partner

- Head contractor

- Water quality advice and design

- Irrigation and pump design and installation

- Surveying services

- Project management

- Civil and structural design

- Geotechnical analysis

- Heritage impact analysis

# Cost

Total cost		 				$1.9 million

Cost per kilolitre					$1.78

Design documentation				$184,800
Diversion						$397,400
Tank							$371,000
Treatment						$766,000
Irrigation connections					$277,000

# Community benefits

The stormwater harvesting system in the Alexandra and Queen Victoria Gardens is an excellent example of how urban landscapes can be retrofitted for sustainable water use. The prominent location of the above ground storage tank shows how we are adapting to a changing climate.

The gardens enhance the character and liveability of Melbourne, contributing social, environmental and economic value to the city. The stormwater harvesting system provides a reliable irrigation source that will sustain the parks regardless of climate change, drought or water restrictions.

The system delivers benefits to all Melburnians by improving the quality of water that enters the Yarra River and Port Phillip Bay.

In addition to reducing pollutants in stormwater runoff, the harvesting system also regulates the flow of stormwater. This prevents flushing of the aquatic habitat in the Yarra following heavy rain.

# Research and planning

The following tasks were completed during the research and planning phase of the project:.

| Water plan | In 2008 a water plan was developed to show different types of vegetated spaces in the gardens and the estimated irrigation requirements. This information was used to design the system. |
| --- | --- |
| Geotechnical survey | A geotechnical assessment carried out in 2009 revealed that underground water storage would not be possible due to unstable soil conditions. This constraint influenced many facets of the final design. |
| MUSIC modelling | Music modelling carried out in 2011 showed that retrofitting the ponds would be an effective method for treating the stormwater. |
| Concept designs | Based on this research, concept designs were created for the system in 2012. This included developing a planting plan to determine the most appropriate water plants for nutrient removal and aesthetic value in a heritage space. |

# Community consultation and engagement

The gardens are a premier event space for Melbourne, so it was essential to inform the community while we were developing the system.

Engagement included many forms, such as:

- Consultation with Heritage Victoria and the skate park operators

- Ongoing discussions with our events management team and the park services

- Installation of project information signs at the site

- Presenting about the scheme at a range of industry conferences and events, and at universities

- Conducting tours of the system with a range of industry figures and groups from local and international organisations.

# Design challenges and constraints

## Unfavourable soil conditions

The gardens are both mainly Coode Island silt, which is not stable enough to support an underground water storage tank. Instead, we used the existing ornamental ponds in Queen Victoria Gardens for storage and treatment. The size of the ponds limited the capacity of the final system design.

## High sediment volumes

The stormwater runoff in this catchment has a high volume of fine sands, which accumulate from the nearby Tan running track and St Kilda Road tram lines. This extra sediment can damage the pump impellers if left untreated. To ensure that sand is removed, we located the gross pollutant trap and sedimentation chamber before the pump.

Road crossing
Due to the unstable soil, we had to position the storage ponds and treated water tank on either side of a major arterial road - Alexander Parade. Getting water from the storage ponds to the tank was a challenge for the design and construction team. With careful mapping of existing cables and a traffic management plan in place, a tunnel was bored under the road at night.

Varying pond elevations 
Working with the existing ornamental ponds in Queen Victoria Gardens presented some challenges. The ponds each have their own elevation, so the water levels are controlled separately. This added complexity to the design and operation of the system.

# Planning approval process

A planning permit was not required, but during the initial design stages, Alexandra and Queen Victoria Gardens were nominated for inclusion in the Victorian Heritage Register. We consulted Heritage Victoria to ensure that the system would not have any adverse impacts on a potentially heritage listed landscape.

# System components

Diversion
Runoff is diverted into the system from an existing 600 mm stormwater drain running under the gardens. The water travels through a gross pollutant trap and into the sedimentation tank. It then flows into the pump well to be transferred to the storage ponds.

When the ponds are full or the diversion network is at capacity, excess stormwater continues down the regular drainage system via an overflow pipe.

Gross pollutant trap
The first structure in the diversion network is a gross pollutant trap, or GPT. Due to the known high volume of fine sand in the water, a Humeguard GPT was placed in front of the pumps, rather than after. It removes course sediment (greater than 150 microns) that might damage the pump impellers.

The GPT removes about 9 per cent of the litter and debris from the water, 99 per cent of the sediment and 20 per cent of the nutrients (nitrogen and phosphorus).

The GPT is inspected every three months and accumulated litter removed. Litter is removed from the GPT by a large truck with a suction hose about three times per year. A typical GPT has a lifespan of ten years. We have included the cost of replacing the GPT into the maintenance budget.

## Sedimentation chamber

The sedimentation chamber is located directly next to the GPT. It allows suspended particles of pollution - fine sands, sediments, oils and hydrocarbons - to settle to the bottom or float to the surface.

The chamber is made of 250 mm thick concrete and was lowered into place using a crane. Like the GPT, it is located before the pumps to protect the pump impellers.

The sedimentation chamber is cleaned out with a suction hose when the depth of sediment measures 0.5 metres.

Ponds
Unlike other stormwater harvesting systems in Melbourne, existing ornamental ponds were used as the primary water storage for this system. The Coode Island silt soil was too unstable to support an underground tank system.

Three ornamental ponds have been retrofitted for stormwater storage, with a total capacity of 1.1 million litres. Partially treated water flows from the diversion system to the first pond, then to the second pond before entering the third pond.

The ponds each have their own elevation, so the water levels are controlled separately through an automated system. Each pond also has a maximum drawdown level. This ensures there is always enough water to prevent algal growth, support healthy plants and maintain the aesthetic value.

The first pond, known as the Children’s Pond, is shallow and primarily used as additional sedimentation area than for high volume storage. The pond is approximately 200 m2 in size. We control the water level in this pond with a permanent weir that allows overflow into the second pond.

The second pond, known as the Nymph Pond, is 1100 m2 in size. It is deeper and functions as both storage and treatment. Wetland plants across the inlet zone and around the perimeter remove nutrients from the water. Similar to a raingarden, the biofilm that forms on the plant stems takes up pollutants, cleaning the water.

We control the water level of this pond with an overflow weir. The drawdown of water from this pond is generally set to 300 mm from the top level. This level is controlled by the central control system and can be varied.

The third pond, known as the Lower Pond, is the largest and deepest. It is 2100 m2 in size and between 500 and 900mm deep. Its primary function is storage, though water plants around the perimeter provide some nutrient stripping as well. A pump is used to transfer water from the lower pond to the biofiltration bed in Alexandra Gardens. It maintains a minimum water level of 300 mm below top level. The diversion pumps shut off automatically when the ponds and the storage tank are full.

To retrofit the ponds, we drained and sealed them to prevent leaking.  The base of each pond was sealed differently due to their construction:

- The Children’s Pond had a concrete base and was painted with waterproofing membrane.

- The Nymph Pond had a clay base liner that was rolled across the base. Rocks, clay and soil for planting were placed on top.

- The Lower Pond held water well throughout the drought and was deemed to be fairly water-tight. Only minimal contouring was carried out to provide more planting opportunities.

## Pumps

Due to the varying elevations of the existing ponds and biofiltration bed, pumps are an essential component for transferring water throughout the system. Two 40 litres per second pumps and one 20 litres per second pump are used to transfer stormwater from the diversion system to the Children’s Pond.

The pumps engage depending on how heavy the rainfall is. In high rain flow events, the full 100 litres per second capacity is used.

Pumps also transfer water between the Lower Pond and the biofiltration bed, and from under the biofiltration bed to the reuse tank.

An automated butterfly valve is used to manage the levels and flows between the Nymph Pond and the Lower Pond.

## Irrigation system

All pumps are controlled by the irrigation central control system.

## Biofiltration bed

The biofiltration bed is constructed the same way as a typical raingarden. It has sand filtration, transition and drainage layers. Unlike a raingarden, the biofiltration bed is surrounded by a one metre tall retaining wall. It is periodically flooded with water from the Lower Pond.

The flooding and resting cycle is based on the detention time of the water. This, in turn, is determined by the hydraulic conductivity of the filter media. The cycle time is pre-set. It is adjusted over time as the filter medium clogs and slows the detention time. Replacing the top of the filter media on an annual basis helps renew the conductivity.

The clean water drains naturally to the pump well. It is then pumped to the above ground storage tank where it is stored for irrigation.

## Tank

The above ground tank is located in Alexandra Gardens, next to the biofiltration bed and public skate park. With a total storage capacity of 230,000 litres, the tank is 4.5 metres tall, 5.5 metres wide and 15 metres long. The UV disinfection, irrigation pumps and control are housed alongside the tank.

Due to the unstable soil we couldn’t place the storage tank underground. However it was construct in the place of a former depot building to ensure that no public open space was lost.

## Plants

Plants are used to take pollutants from the stormwater in the upper and lower ponds, as well as the biofiltration bed. Aquatic plants are used within the ponds, as well as some floating in the centre of the Lower Pond. The collective plant coverage is approximately 1600 m2.

The species used in the ponds include:

- Eleocharis sphacelata

- Acorua gramineus

- Baumea arthrophylla

- Baumea articulate

- Baumea rubiginosa

- Eleocharis acuta

- Eleocharis sphacelata

- Gunnera manicata

- Iris psuedacorus

- Isolepis nodosa

- Isotoma fluviatilis

- Juncus ingens

- Marsilea drummondii

- Myriophyllum crispatum

- Ottelia ovalifolia

- Persicaria decipiens

- Phylidrum lanigunosum

- Potemogeton tricarinatus

- Thalia geniculata var. ruminoides

- Thanlia geniculate

- Triglochin procerum

The top layer of the biofiltration bed was planted with wetland plants, Juncus gregiflorus and Juncus procerus. These native Australian rushes were planted as tube stock, which is cheaper than pre-grown stock allows them to fully establish on site. The grasses are cut back once a year, when the filter medium is replenished.

# Testing and commissioning

The stormwater harvesting system is complex, with main levels that turn pumps and valves on and off. Following completion, it was tested for six months. This included testing for possible problem scenarios and refining the level and pump control system settings.

# Ongoing management

## Maintenance

We carry out regular maintenance of the stormwater harvesting system. Our schedule includes the frequency and location of each activity. Maintenance tasks include:

- Inspecting and cleaning the gross pollutant trap

- Inspecting and cleaning the sedimentation chamber

- Monitor water quality and algae growth in the ponds, especially in summer

- Daily monitoring of the pumps, valves, electrical conductivity meter and pH meter

- Inspecting the tanks using a camera

- Weeding and replacing plants in the biofiltration bed and ponds

- Regular inspection of the ponds and removal of sludge, debris and leaf matter

- Monitoring detention time for filter media and replacing when needed.

## Maintenance cost

Maintenance costs around $33,000 per year. This includes weekly and monthly inspections, removing litter from the gross pollutant trap, replacing plants and filter media, and electricity costs.

## Monitoring

The main purpose of monitoring is to ensure that the water is fit for irrigation.

We included a detailed water monitoring strategy in the operations and maintenance manual.

As a baseline, water quality samples are taken immediately upstream of the diversion point. Our monitoring ensures that the water complies with the Australian Guidelines for Water Recycling - Stormwater Harvesting and Reuse (July 2009), as well as Victorian plumbing standards.

Water quality monitoring is particularly important in this system because the storage ponds are highly visible. Although this will make any water quality problems easy to detect, the problems will also be obvious to garden visitors.

We monitor the water’s pH and salinity levels. Samples are also taken during irrigation season to check for E. coli, turbidity, sodium, chloride, heavy metals and herbicides. We also monitor other water quality indicators, with expected pollutant reductions detailed below.

# Environmental impact

We are committed to creating a water sensitive urban landscape, while also considering any environmental impacts resulting from this infrastructure.

The pumps required to operate the system are powered using electricity, resulting in greenhouse gas emissions.

The estimated power consumption for the pump system is 9157 kWh per year. In line with the city’s Zero Net Emissions strategy, we use carbon offsets to counteract this impact.

# Lessons learnt

#### Soil conditions

The level of soil contamination and structural quality provided many design challenges and drove many of the design outcomes.

#### Reuse tank

Several locations for the reuse tank where considered through the design phase. The final location, where it replaced an underutilised former depot building, was the best compromise for size, constructability and conforming to heritage and aesthetic needs.

#### Managing different levels

Due to the multiple levels of the ponds, the biofiltration bed and the above ground tank, the movement of water between each element requires a valve or pump. This introduced extra complexity.

#### Landscape design

Careful consideration was needed by our landscape designer to insert pits, pipes and other structures without negatively impacting on the overall aesthetic of the gardens.

#### Multiple stages of construction

The interaction between different stages and contractors needed careful management to ensure the best outcomes.

#### Power supply

Power companies are often slow to respond to connection requests and will often not act until electricians issue certificates of compliance. This can cause delays at the end of construction.